## Sheet1
Failure source | Inst. code | Alarm code | Failure detection |  |  | Limit |  |  | Delay |  | Run Mode |  | Fuel mode | Opt. signal | Suppress without Gas system | Overrideable | Remark | Parameter |  | Modbus for parameter |  |  | Modbus address | Forcing Enable | Forcing Value | scale
[5 empty] | Low | High | Hysteresis | Unit |  | Stop | Start | Run | [5 empty] | Limit | Delay | limit | delay | enable
Main FO pressure, engine inlet | PT52 | O | Sensor failure | Fuel oil pressure engine inlet sensor failure |  |  |  |  | 0.5 s | AL | AL | AL | All | [6 empty] | O | O | O | 10637 | 13172 | 13672 | 100
| PT52 | O | Lower than set point | Fuel oil pressure engine inlet low | 4 |  |  | bar | 3 s | AL | AL | AL | All |  |  |  | MDO/MGO | 69100 | 69113 | O | O | O | 10638 | 13172 | 13672 | 100
| PT52 | O | Lower than set point | Fuel oil pressure engine inlet low | 6 |  |  | bar | 3 s | AL | AL | AL | All |  |  |  | HFO | 69101 | 69114 | O | O | O | 10639 | 13172 | 13672 | 100
Main FO pressure, filter inlet | PT51 | O | Sensor failure (PT51) | Fuel oil pressure filter inlet sensor failure |  |  |  |  | 0.5 s | AL | AL | AL | All | [6 empty] | O | O | O | 10635 | 13171 | 13671 | 100
Main FO filter differential pressure | PT51-PT52 | O | Higher than set point | Fuel oil filter differential pressure high |  | 1.5 |  | bar | 5 s | AL | AL | AL | All |  |  |  |  | 69115 | 69116 | O | O | O | 10634 | 13171 | 13671 | 100
Main FO temperature, engine inlet | TE52 | O | Sensor failure | Fuel oil temperature engine inlet sensor failure |  |  |  |  | 0.5 s | AL | AL | AL | All | [6 empty] | O | O | O | 10640 | 13187 | 13687 | 500
| TE52 | O | higher than set point | Fuel oil temperature engine inlet high |  | 155 |  | °C | 5 s | AL | AL | AL | All |  |  |  | HFO | 69120 | 69121 | O | O | O | 10642 | 13187 | 13687 | 10
| TE52 | O | higher than set point | Fuel oil temperature engine inlet high |  | 50 |  | °C | 5 s | AL | AL | AL | All |  |  |  | MDO/MGO | 69102 | 69117 | O | O | O | 10641 | 13187 | 13687 | 10
| TE52 | O | lower than set point | Fuel actuator failure | 20 |  |  | °C | 5 s | AL | AL | AL | Diesel/ Backup |  |  |  | HFO | 69103 | 69118 | O | O | O | 10644 | 13187 | 13687 | 10
Pilot FO pressure, engine inlet | PT32 | O | Sensor failure | Pilot fuel oil pressure engine inlet sensor failure |  |  |  |  | 0.1 s | PT | PT | PT | All |  | O |  |  |  |  | O | O | O | 11605 | 13141 | 13641 | 300
| PT32 | O | Fail to build up | Pilot fuel oil pressure engine inlet build up failure | 500 |  |  | bar | 20 s | - | PT | PT | Diesel/ Gas |  | O |  | Pilot FO pressure fails to build up after activation of MP system | 70310 | 70311 | O | O | O | 11611 | 13141 | 13641 | 1
| PT32 | O | Lower than set point | Pilot fuel oil pressure engine inlet low | 750 |  |  | bar | 3 s | - | PT | PT | Diesel/ Gas |  | O |  | From idle speed | 70304 | 70309 | O | O | O | 11607 | 13141 | 13641 | 1
| PT32 | O | Higher than set point | Pilot fuel oil pressure engine inlet high |  | 1300 |  | bar | 3 s | PT | PT | PT | Diesel/ Gas |  | O |  |  | 70303 | 70308 | O | O | O | 11606 | 13141 | 13641 | 1
| PT32 | O | Deviation from reference: |  | 200 |  |  | bar | 3 s | - | PT | PT | Diesel/ Gas |  | O |  | From idle speed | 70314 | 70315 | - |  |  | 11604 | 13141 | 13641 | 1
Note on O1: JCM: When option is not selected, alarm condition to be suppressed
Note on L2: JungChangMin: Start status means from ECS receive start command to RATED speed reached. If there's speed dependent condition, it is specified
Note on M2: HHI: #1: suppress all AL during stopping phase #2: regard stopping phase same as stop condition
Note on R4: JungChangMin: fuel oil type is dependant on the DI MDO operation selected. delay time to activate new limit value after transition of fue oil type is parameter
Note on R7: JungChangMin: delta P between pilot FO pressure filter inlet and engine inlet is calculated